## INFO
Regional Adequacy Assessment results
Week: | 7
Period start: | 08.02.2020
Period end: | 14.02.2020
Problematic hour: | 128
Used UCTE CGM: | 20200206_0730_FO4_UX0.UCT
Comments: | HU was not included in calculation due to some tool issues. For 9 hours, marked with "0" on sheet "X", RAA optimization could not be performed, since TIC is bigger than Available capacity of the region. Hour 128 of Week07 was intentionally chosen to be critical (instead of hour 90) in order to get less TSOs in HUB and to get bigger difference between TIC and Available capacity (in order to show results of optimisation that are not close to the ERIC limits). PTDF calculations are simulated on CGM for 8th hour of past Thursday (06.02.2020). Some load flow inconsistencies are detected after analysis of the MAP sheet (e.g. sum of imports for RS is not equal to the negative ERIC value of RS) - after deeper analysis of PTDF calculation it is concluded that load flow lossess are differently considered for different TIE-lines (for some interconnectors losses are included in calculation, and for some not). Appropriate changes in algorithm will be applied in upcoming demostrations.
Explanation of document: | RAA results for defined timestamp are organized in several sheets: - ERIC sheet contains following data: ERIC (Expected Remaining/Insufficient Capacity) values - these valus give the expected amount of capacity that is available for export(positive sign)/import(negative sign) ensuring that the system will stay/become adequate, SAIT (System Adequacy Index Target) values - the optimum trade-off between grid investments and potential losses from unserved energy representing the desired level of adequacy defined by each TSO or NRA, - H sheet contains data that explain how critical hour (H) was defined, - X sheet contains following data: HUB - areas with negative ERIC value for defined timestamp (these are importing areas in the PTDF calculation process), TIC (Total Insufficient Capacity) - the absolute value of the region's total expected insufficient capacity, TIF (Total Increase of active power Flow) - total change of active power flows across all observed tie-lines in the region, X (adequacy transactions) - potential transactions from specific area with positive ERIC value to HUB area, required for solving the adequacy issue in a way that active power flows across all network elements of the observed region are minimally altered, - dF sheet contains following data: ∆F - the change of active load flow on specific tie-line, oriented in defined direction - MAP sheet contains following data: border flows, negative ERIC values for areas in HUB and positive X values for areas that are solving adequacy issue.

## ERIC
| SAIT | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 1 | 0.99726 | 0.99726 | 0.99726 | 0.99726 | 0.99726
Date | Hour\Area | AL | BA | BG | GR | HR | HU | ME | MK | RO | RS | SI
2020-02-08 | 1 | 548 | 1762 | 1224 | 2527 | 619 | 0 | -68 | 66 | 2908 | 130 | -348
| 2 | 548 | 1441 | 1452 | 2714 | 761 | 0 | -24 | 176 | 3018 | 430 | -284
| 3 | 548 | 1475 | 1579 | 2917 | 835 | 0 | 21 | 249 | 2781 | 633 | -246
| 4 | 548 | 1466 | 1655 | 2961 | 857 | 0 | 27 | 285 | 2514 | 732 | -250
| 5 | 548 | 1416 | 1658 | 2817 | 830 | 0 | 18 | 287 | 2536 | 664 | -261
| 6 | 548 | 1296 | 1575 | 2487 | 683 | 0 | -11 | 249 | 2001 | 402 | -286
| 7 | 548 | 981 | 1416 | 2284 | 296 | 0 | -48 | 143 | 2068 | 74 | -428
| 8 | 548 | 781 | 1040 | 2061 | 35 | 0 | -97 | 151 | 1663 | -250 | -285
| 9 | 548 | 691 | 838 | 1996 | -110 | 0 | -109 | 72 | 1405 | -484 | -390
| 10 | 548 | 670 | 693 | 1890 | -146 | 0 | -114 | 14 | 1189 | -488 | -425
| 11 | 548 | 694 | 843 | 1659 | -113 | 0 | -122 | 0 | 1371 | -440 | -396
| 12 | 548 | 656 | 655 | 1531 | -128 | 0 | -117 | -7 | 1195 | -367 | -414
| 13 | 548 | 660 | 712 | 1614 | -102 | 0 | -107 | -23 | 1142 | -291 | -395
| 14 | 548 | 713 | 763 | 1156 | -43 | 0 | -100 | -32 | 1153 | -121 | -315
| 15 | 548 | 775 | 743 | 772 | 15 | 0 | -98 | -114 | 1200 | -15 | -256
| 16 | 548 | 812 | 627 | 404 | 64 | 0 | -107 | -93 | 899 | -186 | -239
| 17 | 548 | 750 | 414 | -421 | 24 | 0 | -131 | -70 | 478 | -454 | -291
| 18 | 548 | 624 | 437 | -736 | -191 | 0 | -160 | -140 | 221 | -483 | -350
| 19 | 548 | 537 | 60 | -533 | -271 | 0 | -160 | -132 | 159 | -449 | -396
| 20 | 548 | 499 | 112 | -67 | -290 | 0 | -159 | -123 | 300 | -396 | -335
| 21 | 548 | 579 | 414 | 545 | -226 | 0 | -155 | -78 | 732 | -241 | -287
| 22 | 548 | 688 | 331 | 948 | -181 | 0 | -140 | -66 | 1142 | -252 | -188
| 23 | 548 | 847 | 495 | 1505 | 15 | 0 | -124 | -132 | 1678 | -258 | -209
| 24 | 548 | 1067 | 832 | 1957 | 277 | 0 | -113 | -97 | 1710 | -270 | -113
2020-02-09 | 1 | 699 | 1330 | 1254 | 2019 | 530 | 0 | -78 | 67 | 1767 | 45 | -189
| 2 | 699 | 1455 | 1513 | 2222 | 683 | 0 | -33 | 185 | 1868 | 386 | -131
| 3 | 699 | 1523 | 1639 | 2390 | 763 | 0 | 12 | 254 | 1880 | 630 | -128
| 4 | 699 | 1550 | 1735 | 2388 | 786 | 0 | 23 | 293 | 1843 | 800 | -128
| 5 | 699 | 1546 | 1724 | 2194 | 759 | 0 | 16 | 295 | 1792 | 854 | -140
| 6 | 699 | 1492 | 1667 | 1950 | 617 | 0 | -1 | 254 | 1757 | 733 | -166
| 7 | 699 | 1392 | 1471 | 1824 | 249 | 0 | -44 | 148 | 1669 | 576 | -249
| 8 | 699 | 1314 | 1101 | 1705 | 1 | 0 | -100 | 157 | 1370 | 298 | -66
| 9 | 699 | 1177 | 945 | 1575 | -110 | 0 | -147 | 75 | 1261 | -29 | -194
| 10 | 699 | 1049 | 767 | 1413 | -113 | 0 | -132 | 13 | 1315 | 192 | -253
| 11 | 699 | 952 | 892 | 1377 | -35 | 0 | -159 | -3 | 1375 | -173 | -284
| 12 | 699 | 896 | 703 | 1502 | -3 | 0 | -142 | -15 | 1497 | -103 | -308
| 13 | 699 | 933 | 752 | 1825 | 75 | 0 | -146 | -41 | 1537 | -1 | -258
| 14 | 699 | 1032 | 792 | 1458 | 156 | 0 | -147 | -54 | 1548 | 169 | -172
| 15 | 699 | 1128 | 765 | 1111 | 208 | 0 | -134 | -142 | 1397 | 280 | -154
| 16 | 699 | 1172 | 630 | 830 | 212 | 0 | -127 | -118 | 1083 | 111 | -153
| 17 | 699 | 1120 | 373 | 34 | 112 | 0 | -131 | -89 | 785 | -155 | -170
| 18 | 699 | 972 | 343 | -330 | -146 | 0 | -175 | -153 | 321 | -174 | -263
| 19 | 699 | 870 | -110 | -203 | -266 | 0 | -168 | -141 | 240 | -178 | -331
| 20 | 699 | 818 | -81 | 195 | -296 | 0 | -168 | -163 | 328 | -153 | -321
| 21 | 699 | 863 | 176 | 757 | -220 | 0 | -162 | -89 | 610 | -42 | -273
| 22 | 699 | 937 | 184 | 1230 | -168 | 0 | -150 | -80 | 983 | -47 | -178
| 23 | 699 | 1034 | 417 | 1928 | 35 | 0 | -127 | -149 | 1463 | 28 | -211
| 24 | 699 | 1218 | 784 | 2451 | 303 | 0 | -97 | -117 | 1930 | 174 | -127
2020-02-10 | 1 | 709 | 1404 | 1408 | 2514 | 559 | 0 | -47 | 39 | 1951 | 423 | -196
| 2 | 709 | 1512 | 1684 | 2706 | 714 | 0 | -5 | 178 | 2000 | 756 | -145
| 3 | 709 | 1561 | 1787 | 2833 | 796 | 0 | 31 | 250 | 2055 | 964 | -122
| 4 | 709 | 1570 | 1814 | 2710 | 823 | 0 | 35 | 270 | 2025 | 1080 | -143
| 5 | 709 | 1536 | 1784 | 2123 | 799 | 0 | 20 | 291 | 1766 | 923 | -181
| 6 | 709 | 1396 | 1602 | 1254 | 665 | 0 | -27 | 249 | 1005 | 415 | -326
| 7 | 709 | 1054 | 1100 | 989 | 308 | 0 | -85 | 164 | 483 | -47 | -496
| 8 | 709 | 838 | 515 | 975 | 58 | 0 | -134 | 142 | 40 | -281 | -485
| 9 | 709 | 732 | 395 | 1262 | -74 | 0 | -121 | 58 | -80 | -388 | -510
| 10 | 709 | 705 | 443 | 1544 | -101 | 0 | -151 | -7 | -170 | -308 | -484
| 11 | 709 | 726 | 616 | 1732 | -68 | 0 | -145 | -29 | 183 | -271 | -489
| 12 | 709 | 682 | 441 | 1880 | -104 | 0 | -133 | -45 | 496 | -205 | -488
| 13 | 709 | 687 | 539 | 2024 | -93 | 0 | -119 | -71 | 576 | -130 | -492
| 14 | 709 | 730 | 544 | 1738 | -32 | 0 | -107 | -87 | 482 | 326 | -454
| 15 | 709 | 786 | 497 | 1577 | 26 | 0 | -100 | -180 | 802 | 114 | -381
| 16 | 709 | 823 | 396 | 1430 | 68 | 0 | -97 | -150 | 757 | -89 | -415
| 17 | 709 | 761 | 180 | 772 | 22 | 0 | -118 | -115 | 269 | -396 | -440
| 18 | 709 | 635 | 273 | 427 | -193 | 0 | -150 | -172 | 345 | -418 | -530
| 19 | 709 | 550 | -82 | 572 | -278 | 0 | -154 | -157 | -13 | -400 | -534
| 20 | 709 | 512 | -49 | 1125 | -295 | 0 | -151 | -149 | -9 | -329 | -500
| 21 | 709 | 594 | 217 | 1841 | -226 | 0 | -152 | -101 | 458 | -197 | -407
| 22 | 709 | 709 | 207 | 2285 | -180 | 0 | -139 | -94 | 838 | -230 | -272
| 23 | 709 | 872 | 423 | 2959 | 12 | 0 | -126 | -168 | 1474 | -231 | -337
| 24 | 709 | 1094 | 768 | 3401 | 273 | 0 | -109 | -130 | 2184 | -187 | -216
2020-02-11 | 1 | 679 | 1316 | 1571 | 3354 | 519 | 0 | -46 | 67 | 2131 | 157 | -289
| 2 | 679 | 1436 | 1826 | 3448 | 663 | 0 | -4 | 190 | 2355 | 463 | -239
| 3 | 679 | 1490 | 1947 | 3473 | 733 | 0 | 48 | 260 | 2334 | 669 | -203
| 4 | 679 | 1500 | 1984 | 3280 | 750 | 0 | 53 | 294 | 2194 | 715 | -217
| 5 | 679 | 1471 | 1943 | 2654 | 720 | 0 | 40 | 297 | 1930 | 575 | -247
| 6 | 679 | 1342 | 1793 | 1709 | 573 | 0 | -9 | 253 | 1544 | 146 | -377
| 7 | 679 | 1018 | 1325 | 1349 | 202 | 0 | -68 | 136 | 760 | -227 | -692
| 8 | 679 | 814 | 811 | 1228 | -27 | 0 | -109 | 138 | 87 | -405 | -495
| 9 | 679 | 723 | 775 | 1415 | -146 | 0 | -104 | 56 | -74 | -477 | -511
| 10 | 679 | 704 | 755 | 1639 | -166 | 0 | -127 | -6 | 35 | -444 | -490
| 11 | 679 | 727 | 918 | 1782 | -104 | 0 | -128 | -22 | -104 | -369 | -547
| 12 | 679 | 688 | 697 | 1896 | -117 | 0 | -121 | -45 | -15 | -290 | -560
| 13 | 679 | 697 | 798 | 1993 | -84 | 0 | -115 | -84 | 29 | -210 | -558
| 14 | 679 | 740 | 819 | 1641 | -25 | 0 | -105 | -108 | -19 | -92 | -480
| 15 | 679 | 796 | 796 | 1302 | 26 | 0 | -99 | -207 | 380 | -58 | -393
| 16 | 679 | 831 | 658 | 878 | 63 | 0 | -113 | -175 | 705 | -286 | -429
| 17 | 679 | 769 | 470 | 54 | 13 | 0 | -137 | -132 | 1044 | -625 | -422
| 18 | 679 | 643 | 573 | -368 | -194 | 0 | -180 | -188 | 644 | -668 | -548
| 19 | 679 | 557 | 216 | -309 | -325 | 0 | -184 | -172 | 494 | -638 | -580
| 20 | 679 | 517 | 228 | 277 | -347 | 0 | -180 | -166 | 731 | -564 | -592
| 21 | 679 | 595 | 504 | 984 | -270 | 0 | -170 | -111 | 991 | -423 | -472
| 22 | 679 | 707 | 455 | 1453 | -219 | 0 | -152 | -107 | 1590 | -412 | -366
| 23 | 679 | 870 | 663 | 2234 | -18 | 0 | -132 | -186 | 2438 | -358 | -423
| 24 | 679 | 1091 | 1043 | 2764 | 250 | 0 | -119 | -150 | 1588 | -283 | -299
2020-02-12 | 1 | 668 | 1312 | 1624 | 2786 | 499 | 0 | -100 | 61 | 1585 | 42 | -519
| 2 | 668 | 1430 | 1869 | 2941 | 648 | 0 | -37 | 188 | 1694 | 345 | -475
| 3 | 668 | 1483 | 1983 | 3011 | 725 | 0 | 14 | 259 | 1795 | 571 | -431
| 4 | 668 | 1490 | 2017 | 2872 | 747 | 0 | 17 | 292 | 1834 | 622 | -434
| 5 | 668 | 1460 | 1974 | 2314 | 721 | 0 | 4 | 295 | 1723 | 468 | -481
| 6 | 668 | 1331 | 1826 | 1409 | 577 | 0 | -39 | 249 | 1088 | 20 | -585
| 7 | 668 | 1006 | 1365 | 1130 | 232 | 0 | -95 | 161 | 265 | -376 | -936
| 8 | 668 | 801 | 858 | 1098 | -24 | 0 | -139 | 145 | -293 | -557 | -719
| 9 | 668 | 711 | 825 | 1383 | -149 | 0 | -124 | 62 | -486 | -618 | -743
| 10 | 668 | 692 | 806 | 1669 | -173 | 0 | -149 | -1 | -454 | -571 | -723
| 11 | 668 | 716 | 967 | 1883 | -149 | 0 | -140 | -16 | -70 | -499 | -736
| 12 | 668 | 676 | 744 | 2018 | -179 | 0 | -125 | -41 | 168 | -429 | -730
| 13 | 668 | 685 | 842 | 2122 | -153 | 0 | -109 | -82 | 277 | -347 | -806
| 14 | 668 | 731 | 865 | 1817 | -87 | 0 | -98 | -110 | 539 | -202 | -778
| 15 | 668 | 788 | 857 | 1581 | -22 | 0 | -91 | -221 | 719 | -112 | -703
| 16 | 668 | 826 | 736 | 1287 | 31 | 0 | -89 | -187 | 1008 | -291 | -616
| 17 | 668 | 764 | 559 | 509 | -5 | 0 | -107 | -140 | 782 | -593 | -634
| 18 | 668 | 638 | 659 | 81 | -201 | 0 | -150 | -193 | 516 | -603 | -724
| 19 | 668 | 552 | 309 | 184 | -308 | 0 | -156 | -176 | 757 | -558 | -791
| 20 | 668 | 510 | 329 | 698 | -312 | 0 | -155 | -169 | 947 | -475 | -774
| 21 | 668 | 590 | 609 | 1395 | -222 | 0 | -149 | -114 | 1524 | -318 | -661
| 22 | 668 | 699 | 562 | 1851 | -166 | 0 | -130 | -136 | 2184 | -302 | -537
| 23 | 668 | 859 | 767 | 2561 | 7 | 0 | -109 | -193 | 2540 | -255 | -567
| 24 | 668 | 1078 | 1142 | 3155 | 245 | 0 | -92 | -162 | 1326 | -183 | -476
2020-02-13 | 1 | 658 | 1298 | 1622 | 3197 | 474 | 0 | -33 | 55 | 1300 | 135 | -439
| 2 | 658 | 1415 | 1878 | 3379 | 638 | 0 | 18 | 187 | 1386 | 441 | -337
| 3 | 658 | 1467 | 1989 | 3467 | 727 | 0 | 63 | 256 | 1460 | 660 | -325
| 4 | 658 | 1475 | 2017 | 3347 | 761 | 0 | 68 | 290 | 1376 | 703 | -325
| 5 | 658 | 1445 | 1974 | 2805 | 754 | 0 | 54 | 292 | 1032 | 537 | -368
| 6 | 658 | 1315 | 1826 | 1947 | 681 | 0 | 11 | 246 | 396 | 69 | -512
| 7 | 658 | 989 | 1364 | 1591 | 507 | 0 | -48 | 168 | -219 | -347 | -861
| 8 | 658 | 793 | 854 | 1380 | 360 | 0 | -91 | 154 | -553 | -546 | -665
| 9 | 658 | 702 | 825 | 1434 | 144 | 0 | -74 | 62 | -520 | -625 | -635
| 10 | 658 | 687 | 810 | 1477 | 50 | 0 | -108 | -14 | -464 | -594 | -546
| 11 | 658 | 703 | 976 | 1394 | 23 | 0 | -108 | -50 | -271 | -524 | -523
| 12 | 658 | 659 | 753 | 1372 | 37 | 0 | -96 | -74 | -177 | -443 | -512
| 13 | 658 | 660 | 851 | 1458 | 96 | 0 | -88 | -119 | -50 | -353 | -528
| 14 | 658 | 702 | 873 | 1023 | 203 | 0 | -77 | -148 | 152 | -214 | -471
| 15 | 658 | 754 | 845 | 625 | 307 | 0 | -68 | -249 | 116 | -142 | -391
| 16 | 658 | 783 | 707 | 268 | 349 | 0 | -68 | -217 | 73 | -345 | -379
| 17 | 658 | 703 | 529 | -386 | 303 | 0 | -91 | -185 | -154 | -665 | -435
| 18 | 658 | 566 | 644 | -743 | 80 | 0 | -136 | -245 | -454 | -673 | -571
| 19 | 658 | 514 | 295 | -681 | -80 | 0 | -138 | -227 | -502 | -623 | -652
| 20 | 658 | 497 | 314 | -232 | -110 | 0 | -136 | -224 | -492 | -539 | -651
| 21 | 658 | 573 | 593 | 459 | -57 | 0 | -135 | -167 | -73 | -387 | -569
| 22 | 658 | 664 | 541 | 897 | -20 | 0 | -124 | -163 | 474 | -368 | -422
| 23 | 658 | 828 | 745 | 1699 | 124 | 0 | -104 | -233 | 994 | -303 | -479
| 24 | 658 | 1049 | 1120 | 2266 | 359 | 0 | -90 | -192 | 1490 | -226 | -337
2020-02-14 | 1 | 657 | 1263 | 1505 | 2283 | 562 | 0 | -50 | 40 | 1566 | -448 | -389
| 2 | 657 | 1380 | 1757 | 2443 | 719 | 0 | -4 | 174 | 1583 | -82 | -363
| 3 | 657 | 1434 | 1866 | 2518 | 809 | 0 | 45 | 242 | 1632 | 250 | -294
| 4 | 657 | 1445 | 1894 | 2410 | 850 | 0 | 49 | 275 | 1609 | 497 | -335
| 5 | 657 | 1415 | 1850 | 1900 | 851 | 0 | 32 | 279 | 1280 | 562 | -355
| 6 | 657 | 1286 | 1692 | 1000 | 801 | 0 | -13 | 233 | 626 | 404 | -469
| 7 | 657 | 969 | 1214 | 580 | 703 | 0 | -75 | 154 | 48 | -78 | -790
| 8 | 657 | 765 | 692 | 257 | 615 | 0 | -120 | 135 | -385 | -512 | -602
| 9 | 657 | 678 | 660 | 294 | 418 | 0 | -113 | 45 | -333 | -728 | -572
| 10 | 657 | 662 | 651 | 367 | 266 | 0 | -138 | -26 | -346 | -809 | -515
| 11 | 657 | 677 | 821 | 380 | 155 | 0 | -138 | -49 | -283 | -772 | -543
| 12 | 657 | 630 | 596 | 475 | 154 | 0 | -125 | -77 | -171 | -694 | -517
| 13 | 657 | 624 | 689 | 688 | 251 | 0 | -118 | -121 | -195 | -611 | -475
| 14 | 657 | 657 | 701 | 356 | 408 | 0 | -114 | -152 | -55 | -518 | -454
| 15 | 657 | 724 | 668 | 203 | 532 | 0 | -109 | -251 | -12 | -379 | -415
| 16 | 657 | 759 | 537 | 33 | 587 | 0 | -109 | -218 | -24 | -319 | -391
| 17 | 657 | 689 | 350 | -641 | 548 | 0 | -129 | -185 | -193 | -542 | -453
| 18 | 657 | 583 | 450 | -920 | 310 | 0 | -167 | -246 | -526 | -887 | -542
| 19 | 657 | 504 | 90 | -623 | 112 | 0 | -178 | -228 | -541 | -918 | -588
| 20 | 657 | 495 | 110 | -3 | 19 | 0 | -175 | -226 | -483 | -893 | -528
| 21 | 657 | 577 | 402 | 731 | 16 | 0 | -160 | -168 | -77 | -832 | -443
| 22 | 657 | 678 | 368 | 1234 | 25 | 0 | -138 | -161 | 364 | -691 | -298
| 23 | 657 | 816 | 582 | 1967 | 172 | 0 | -117 | -229 | 918 | -692 | -313
| 24 | 657 | 1019 | 974 | 2549 | 433 | 0 | -100 | -181 | 918 | -647 | -242

## H
Hour in Week | Hour in day | Areas in HUB | TIC for day [MW] | Available capacity [MW] | Opmisation possible? (0=No, 1=Yes)
162 | 18 | 6 | -3288 | 2000 | 0
163 | 19 | 6 | -3076 | 1363 | 0
139 | 19 | 7 | -2903 | 1467 | 0
138 | 18 | 6 | -2822 | 1948 | 0
140 | 20 | 7 | -2384 | 1469 | 0
164 | 20 | 6 | -2308 | 1281 | 0
91 | 19 | 6 | -2208 | 1946 | 0
90 | 18 | 6 | -2146 | 2539 | 1
161 | 17 | 6 | -2143 | 2244 | 1
105 | 9 | 5 | -2120 | 3649 | 1
106 | 10 | 6 | -2071 | 3835 | 1
18 | 18 | 6 | -2060 | 1830 | 0
115 | 19 | 5 | -1989 | 2470 | 1
19 | 19 | 6 | -1941 | 1304 | 0
137 | 17 | 6 | -1916 | 2193 | 1
116 | 20 | 5 | -1885 | 3152 | 1
114 | 18 | 5 | -1871 | 2562 | 1
128 | 8 | 4 | -1855 | 4199 | 1
129 | 9 | 4 | -1854 | 3825 | 1
92 | 20 | 5 | -1849 | 2432 | 1
154 | 10 | 5 | -1834 | 2603 | 1
155 | 11 | 5 | -1785 | 2690 | 1
153 | 9 | 4 | -1746 | 2752 | 1
104 | 8 | 5 | -1732 | 3570 | 1
130 | 10 | 5 | -1726 | 3682 | 1
165 | 21 | 5 | -1680 | 2383 | 1
152 | 8 | 4 | -1619 | 3121 | 1
67 | 19 | 7 | -1618 | 1831 | 1
107 | 11 | 6 | -1610 | 4234 | 1
156 | 12 | 5 | -1584 | 2512 | 1
157 | 13 | 5 | -1520 | 2909 | 1
108 | 12 | 5 | -1504 | 4274 | 1
109 | 13 | 5 | -1497 | 4594 | 1
68 | 20 | 7 | -1482 | 2346 | 1
113 | 17 | 5 | -1479 | 3282 | 1
131 | 11 | 5 | -1476 | 3754 | 1
127 | 7 | 4 | -1475 | 5277 | 1
117 | 21 | 5 | -1464 | 4786 | 1
66 | 18 | 5 | -1463 | 2389 | 1
93 | 21 | 5 | -1446 | 3753 | 1
103 | 7 | 3 | -1407 | 4827 | 1
43 | 19 | 7 | -1397 | 1809 | 1
141 | 21 | 6 | -1388 | 2283 | 1
20 | 20 | 6 | -1370 | 1459 | 1
17 | 17 | 5 | -1367 | 2214 | 1
167 | 23 | 4 | -1351 | 5112 | 1
89 | 17 | 4 | -1316 | 3029 | 1
81 | 9 | 5 | -1312 | 3648 | 1
132 | 12 | 5 | -1302 | 3479 | 1
158 | 14 | 5 | -1293 | 2779 | 1
166 | 22 | 4 | -1288 | 3326 | 1
110 | 14 | 5 | -1275 | 4620 | 1
83 | 11 | 6 | -1274 | 4106 | 1
118 | 22 | 5 | -1271 | 5964 | 1
94 | 22 | 5 | -1256 | 4884 | 1
42 | 18 | 6 | -1241 | 2335 | 1
82 | 10 | 5 | -1233 | 3812 | 1
58 | 10 | 6 | -1221 | 3401 | 1
112 | 16 | 4 | -1183 | 4556 | 1
44 | 20 | 6 | -1182 | 2040 | 1
10 | 10 | 4 | -1173 | 5004 | 1
57 | 9 | 5 | -1173 | 3156 | 1
168 | 0 | 4 | -1170 | 6550 | 1
159 | 15 | 5 | -1166 | 2784 | 1
111 | 15 | 5 | -1149 | 4613 | 1
84 | 12 | 6 | -1148 | 3960 | 1
133 | 13 | 5 | -1138 | 3723 | 1
119 | 23 | 4 | -1124 | 7402 | 1
143 | 23 | 4 | -1119 | 5048 | 1
95 | 23 | 5 | -1117 | 6884 | 1
142 | 22 | 5 | -1097 | 3234 | 1
9 | 9 | 4 | -1093 | 5550 | 1
69 | 21 | 5 | -1083 | 3819 | 1
11 | 11 | 4 | -1071 | 5115 | 1
65 | 17 | 4 | -1069 | 2713 | 1
160 | 16 | 5 | -1061 | 2573 | 1
85 | 13 | 5 | -1051 | 4196 | 1
80 | 8 | 4 | -1036 | 3757 | 1
12 | 12 | 5 | -1033 | 4585 | 1
136 | 16 | 4 | -1009 | 2838 | 1
88 | 16 | 4 | -1003 | 3814 | 1
59 | 11 | 5 | -1002 | 3966 | 1
21 | 21 | 5 | -987 | 2818 | 1
79 | 7 | 3 | -987 | 5469 | 1
60 | 12 | 5 | -975 | 4208 | 1
151 | 7 | 3 | -943 | 4325 | 1
13 | 13 | 5 | -918 | 4676 | 1
70 | 22 | 5 | -915 | 4748 | 1
120 | 0 | 4 | -913 | 7614 | 1
134 | 14 | 4 | -910 | 3611 | 1
61 | 13 | 5 | -905 | 4535 | 1
56 | 8 | 3 | -900 | 3277 | 1
145 | 1 | 3 | -887 | 7876 | 1
71 | 23 | 4 | -862 | 6449 | 1
96 | 0 | 4 | -851 | 7415 | 1
135 | 15 | 4 | -850 | 3305 | 1
144 | 0 | 4 | -845 | 6942 | 1
86 | 14 | 6 | -829 | 3879 | 1
22 | 22 | 5 | -827 | 3657 | 1
45 | 21 | 5 | -786 | 3105 | 1
87 | 15 | 4 | -757 | 3979 | 1
64 | 16 | 4 | -751 | 4183 | 1
23 | 23 | 4 | -723 | 5088 | 1
62 | 14 | 4 | -680 | 4529 | 1
63 | 15 | 3 | -661 | 4511 | 1
35 | 11 | 5 | -654 | 5295 | 1
72 | 0 | 4 | -642 | 8429 | 1
8 | 8 | 3 | -632 | 6279 | 1
55 | 7 | 3 | -628 | 4807 | 1
16 | 16 | 4 | -625 | 3354 | 1
102 | 6 | 2 | -624 | 7168 | 1
46 | 22 | 5 | -623 | 4033 | 1
97 | 1 | 2 | -619 | 8577 | 1
14 | 14 | 5 | -611 | 4333 | 1
24 | 0 | 4 | -593 | 6391 | 1
36 | 12 | 5 | -571 | 5297 | 1
41 | 17 | 4 | -545 | 3123 | 1
98 | 2 | 2 | -512 | 9783 | 1
126 | 6 | 1 | -512 | 7149 | 1
34 | 10 | 3 | -498 | 5448 | 1
47 | 23 | 3 | -487 | 5604 | 1
15 | 15 | 4 | -483 | 4053 | 1
150 | 6 | 2 | -482 | 6699 | 1
101 | 5 | 1 | -481 | 9627 | 1
33 | 9 | 4 | -480 | 5732 | 1
7 | 7 | 2 | -476 | 7810 | 1
121 | 1 | 2 | -472 | 8739 | 1
146 | 2 | 3 | -449 | 8713 | 1
37 | 13 | 4 | -446 | 5821 | 1
100 | 4 | 1 | -434 | 10559 | 1
99 | 3 | 1 | -431 | 10509 | 1
39 | 15 | 3 | -430 | 5588 | 1
1 | 1 | 2 | -416 | 9784 | 1
40 | 16 | 3 | -398 | 4737 | 1
78 | 6 | 2 | -386 | 8039 | 1
38 | 14 | 3 | -373 | 5854 | 1
125 | 5 | 1 | -368 | 9551 | 1
149 | 5 | 1 | -355 | 8826 | 1
54 | 6 | 2 | -353 | 7295 | 1
48 | 0 | 3 | -341 | 7559 | 1
122 | 2 | 1 | -337 | 10000 | 1
73 | 1 | 2 | -335 | 9794 | 1
148 | 4 | 1 | -335 | 9686 | 1
123 | 3 | 1 | -325 | 10747 | 1
124 | 4 | 1 | -325 | 10695 | 1
2 | 2 | 2 | -308 | 10540 | 1
6 | 6 | 2 | -297 | 9241 | 1
147 | 3 | 1 | -294 | 9453 | 1
31 | 7 | 2 | -293 | 8028 | 1
25 | 1 | 2 | -267 | 7711 | 1
5 | 5 | 1 | -261 | 10774 | 1
4 | 4 | 1 | -250 | 11045 | 1
77 | 5 | 1 | -247 | 10309 | 1
3 | 3 | 1 | -246 | 11038 | 1
49 | 1 | 2 | -243 | 9007 | 1
74 | 2 | 2 | -243 | 11060 | 1
76 | 4 | 1 | -217 | 11449 | 1
75 | 3 | 1 | -203 | 11633 | 1
53 | 5 | 1 | -181 | 9951 | 1
30 | 6 | 2 | -167 | 9169 | 1
32 | 8 | 2 | -166 | 6645 | 1
26 | 2 | 2 | -164 | 9011 | 1
50 | 2 | 2 | -150 | 10259 | 1
52 | 4 | 1 | -143 | 11036 | 1
29 | 5 | 1 | -140 | 9879 | 1
27 | 3 | 1 | -128 | 9790 | 1
28 | 4 | 1 | -128 | 10117 | 1
51 | 3 | 1 | -122 | 10986 | 1

## X
HUB: | ME, RO, RS, SI
TIC [MW] | 1855
TIF [MW] | 2621.0436
Transaction direction | X [MW] | ERIC [MW]
AL>HUB | 94.5581 | 658
BA>HUB | 603.2682 | 793
BG>HUB | 615.2147 | 854
GR>HUB | 29.7531 | 1380
HR>HUB | 360 | 360
HU>HUB | 0 | 0
MK>HUB | 152.2059 | 154

## dF
Border direction | Border flow [MW] | TIE line name | ΔF[MW]
SIàEU | -111.72 | TIE 220kV Padriciano - Divača | 6.6565
|  | TIE 400kV Redipuglia - Divača | -4.3534
|  | TIE 400kV Maribor - Kainachtal (1) | -45.0912
|  | TIE 400kV Maribor - Kainachtal (2) | -45.0912
|  | TIE 220kV Podlog - Obersielach | -23.8434
SIàHR | -556.08 | TIE 220kV Cirkovice - Žerjavinec | -41.273
|  | TIE 400kV Krško - Tumbri (1) | -173.9748
|  | TIE 400kV Krško - Tumbri (2) | -173.9748
|  | TIE 220kV Divača - Pehlin | -51.5595
|  | TIE 400kV Divača - Melina | -115.2958
EUàHU | -109.51 | TIE 750kV Zakhidnoukrainska - Szabolcsbáka | 0
|  | TIE 400kV Levice - God | -21.7709
|  | TIE 400kV Gabčikovo - Gyor | -2.8245
|  | TIE 400kV Zurndorf - Gyor | -32.9751
|  | TIE 220kV Neusiedl - Gyor | -6.4996
|  | TIE 220kV Wien Sudost - Gyor | -5.7138
|  | TIE 220kV Mukacheve - Kisvarna | -1.4921
|  | TIE 400kV Mukacheve - Szabolcsbáka | -7.664
|  | TIE 400kV Zurndorf - Szombathely | -29.3567
|  | TIE 220kV Mukacheve - Tiszalok | -1.2136
ROàHU | -12.48 | TIE 400kV Arad - Sandorfalva | -14.5958
|  | TIE 400kV Nadab - Bekescsaba | 2.1179
RSàHU | 28.61 | TIE 400kV Subotica 3 - Sandorfalva | 28.6113
HRàHU | 93.38 | TIE 400kV Ernestinovo - Peks (1) | 0
|  | TIE 400kV Ernestinovo - Peks (2) | 98.8994
|  | TIE 400kV Žerjavinec - Heviz (1) | 0
|  | TIE 400kV Žerjavinec - Heviz (2) | -5.5209
HRàBA | -289.46 | TIE 220kV Zakučac - Mostar 4 | 0
|  | TIE 220kV Sisak - Prijedor | -33.557
|  | TIE 220kV Đakovo - Gradačac | -19.3828
|  | TIE 400kV Konjsko - Mostar 4 | -49.5946
|  | TIE 220kV Međurić - Prijedor | -29.0481
|  | TIE 220kV Plat - Trebinje | 5.1623
|  | TIE 220kV Đakovo - Tuzla | -23.5557
|  | TIE 400kV Ernestinovo - Ugljevik | -121.267
|  | TIE 110kV Buško Blato - Livno | -3.6873
|  | TIE 110kV S. Brod - B. Brod | -10.9244
|  | TIE 110kV Opuzen - Čapljina | 0.18844
|  | TIE 110kV Imotski - Grude | -2.1746
|  | TIE 110kV Knin - B. Grahovo | 3.5938
|  | TIE 110kV Gračac - EVP Kulen Vakuf | -1.0951
|  | TIE 110kV Opuzen - Neum | -0.12562
|  | TIE 110kV Ston - Neum | 0.12562
|  | TIE 110kV Županja - Orašje | -9.6492
|  | TIE 110kV Komolac - Trebinje | 5.2273
|  | TIE 110kV Vrgorac - Ljubuški | 0.30759
HRàRS | 0 | TIE 400kV Ernestinovo - S. Mitrovica | 1.3214e-14
|  | TIE 110kV Beli Manastir - Apatin | 0
|  | TIE 110kV Nijemci - Šid | 0
BAàME | 83.58 | TIE 220kV Sarajevo 20 - HE Piva | 24.2645
|  | TIE 400kV Trebinje - Lastva | 34.0345
|  | TIE 220kV Trebinje - HE Perućica | 15.3348
|  | TIE 110kV Trebinje - Herceg Novi | 3.5989
|  | TIE 110kV Bileća - Čvor Vilusi (Nikšić) | 6.3516
BAàRS | 230.23 | TIE 400kV Ugljevik - S. Mitrovica | 158.1173
|  | TIE 220kV Višegrad - Vardište | 40.1791
|  | TIE 110kV Zvornik - Mali Zvornik | 16.6145
|  | TIE 110kV Bijeljina 4 (Janja) - Lešnica | 15.3145
RSàME | -51.72 | TIE 400kV Peć 3 - Ribarevine | -11.9039
|  | TIE 220kV Bajina Bašta - Pljevlja 2 | -24.8902
|  | TIE 220kV Požega - Pljevlja 2 | -13.051
|  | TIE 110kV Potpeć - Pljevlja 1 | -1.8755
MEàAL | -60.89 | TIE 400kV Podgorica 2 - Tirana 2 | -35.2008
|  | TIE 220kV Podgorica 1 - Koplik | -25.6849
BGàRO | 516.3 | TIE 400kV Kozloduy - Tantareni (2) | 0
|  | TIE 400kV Kozloduy - Tantareni (1) | 287.7084
|  | TIE 400kV Varna - Stupina | 117.166
|  | TIE 400kV Dobrudzha - Rahman | 111.4225
ROàEU | 2.21 | TIE 400kV Rosiori - Mukacheve | 2.2102
RSàRO | 29.93 | TIE 400kV HE Đerdap 1 - Portile de Fier | 29.9342
RSàBG | -107.46 | TIE 400kV Niš 2 - Sofia Zapad | -107.4561
MKàBG | 0 | TIE 400kV Štip - Ch.Mogila | -4.6135e-15
|  | TIE 110kV Susica - Petrich | 0
|  | TIE 110kV K. Palanka - Skakavitsa | 0
GRàBG | 22.01 | TIE 400kV Thessaloniki - Blagoevgrad | 22.0087
MKàRS | 174.64 | TIE 400kV Štip - Vranje 4 | 77.3055
|  | TIE 400kV Skopje 4 - Uroševac 2 | 97.3341
RSàAL | -32.45 | TIE 220kV Prizren 2 - Fierza | -32.4522
|  | TIE 400kV Koman - Kosovo B | 0
GRàAL | -1.22 | TIE 400kV Kardia - Zemlak | -2.1269e-14
|  | TIE 110kV Mourtos - Bistrica | -1.2197
MKàGR | -22.43 | TIE 400kV Bitola - Meliti | -2.6314e-15
|  | TIE 400kV Dubrovo - Thessaloniki | -22.4348
GRàTR | -13.47 | TIE 400kV N. Santa - Babaeski | -13.4699
BGàTR | 13.47 | TIE 400kV Maritsa Iztok 3 - Hamitabat (1) | 5.8763
|  | TIE 400kV Maritsa Iztok 3 - Hamitabat (2) | 7.5935

## MAP
*In order to properly display data, zoom value should be 60%.
[47 empty] | å | ã | æ
[47 empty] | á |  | â
[47 empty] | ç | ä | è
ã
2.21
ã
109.51
â
[13 empty] | HU | [9 empty] | 12.48
[12 empty] | 0 | [26 empty] | RO
-553
111.72
|  |  | è | [14 empty] | ã
93.38
28.61
|  | SI | [6 empty] | æ
å
| -665 | [5 empty] | HR | [7 empty] | â
|  |  |  | 556.08 | [21 empty] | æ
[6 empty] | 360 | [6 empty] | 0
29.93
ã
289.46
[17 empty] | â | [6 empty] | RS | [18 empty] | ã
[11 empty] | BA |  |  |  | 230.23 | [7 empty] | -546 | [17 empty] | 516.3
603.2682
[19 empty] | 51.72 | [15 empty] | á
BG
[13 empty] | 83.58 | [6 empty] | æ | [12 empty] | 107.46
[42 empty] | 615.2147 |  |  |  | è
[15 empty] | è |  |  | ME
13.47
-91
[22 empty] | 32.45 | [11 empty] | 0
[20 empty] | å | [8 empty] | å
[24 empty] | æ | [11 empty] | æ
[19 empty] | 60.89 | [8 empty] | 174.64 | [13 empty] | ã
á
[30 empty] | MK | [9 empty] | 22.01
13.47
152.2059
[22 empty] | AL | [10 empty] | ã
[21 empty] | 94.5581 | [10 empty] | 22.43
GR
è
29.7531
1.22
1
1